## Sheet1
How to evaluate the section of one cable |  |  |  | Norm Americain
p | Conductivie (56 Cu) (35 Al) |  |  | AWG => 3A/mm2
S | Section [mm2]
I | Courent [A]
cosj | For DC courant = 1
e | Voltage loss inside the cable [V]
L | Length [m]
|  | Norme AWG | Diamètre mm | Section mm² | Current A
L [m] | 15 | 1 | 7,35 mm | 42,40 mm² | 127 A
I [A] | 2 | 2 | 6,54 mm | 33,60 mm² | 100 A
V max | 24 | 4 | 5,19 mm | 21,20 mm² | 64 A
cosj | 1 | 6 | 4,11 mm | 13,30 mm² | 40 A
p | 56 | 8 | 3,26 mm | 8,35 mm² | 25 A
S Calculé | 0.44643 | 10 | 2,59 mm | 5,26 mm² | 16 A
Diameter | 0.75412 | 12 | 2,05 mm | 3,31 mm² | 10 A
AVG | 20.6364 | 14 | 1,63 mm | 2,08 mm² | 6.2 A
e [V] | 1.2 | 16 | 1,30 mm | 1,31 mm² | 3.9 A
|  | 18 | 1,02 mm | 0,83 mm² | 2.5 A
|  | 20 | 0.813 mm | 0.51 mm² | 1.55 A
|  | 25 | 0.455 mm | 0.16 mm² | 0.48 A
Input data |  | 32 | 0.203 mm | 0.03 mm² | 97 mA
|  | 38 | 0.102 mm | 0,008 mm² | 24.5 mA
|  | 24 | 0.50981 | 0.20402 | 0.61207
|  | 21.6954 | 0.92155 | 0.66667 | 2
|  | 20.6364 | 0.75412 | 0.44643 | 1.3393
MG 11/3/2002
Note on D25: Insert your AVG value
Note on G25: From AWG estimation take in account security factor
Note on G29: From AWG estimation take in account security factor
Note on G27: Insert your current
Note on D27: Estimation from AWG including security factor
I x L x cosj e= ------------------ p x S
I x L x cosj S= ------------------ p x e